## UI
Wire Calculator for Polyphase AC Circuits
|  | source voltage | 208 | V
|  | line phase | 3
|  | load in power or current | 200 | A
|  | length from source to load | 100 | ft
|  | power factor | 0.8
|  | ambient temperature | 86 | F
|  | insulation temperature rating | 167 [ 75 ] | F [ C ]
|  | direct burry conduit type, open air? | steel conduit
|  | number of parallel conductor set(s) | 1
|  | conductors per raceway or cable | 2-3
|  | maximum voltage drop target | 3 | %
|  | upsize #3AWG wire to #2AWG wire | yes
Aluminum Conductors
|  | conductor current | 200 | A
|  | conductor area | 250000 | CM
|  | conductor size | 250 | MCM
|  | equipment grounding conductor | 4 | AWG
|  | bonding conductor and jumper | 2 | AWG
|  | grounding electrode conductor | 2 | AWG
|  | voltage drop | 1.6654 | %
|  | volts at load | 204.5359 | V
|  | maximum allowable length | 180.1333 | ft
Copper Conductors
|  | conductor current | 200 | A
|  | conductor area | 167800 | CM
|  | conductor size | 3/0 | AWG
|  | equipment grounding conductor | 6 | AWG
|  | bonding conductor and jumper | 4 | AWG
|  | grounding electrode conductor | 4 | AWG
|  | voltage drop | 1.5722 | %
|  | volts at load | 204.7299 | V
|  | maximum allowable length | 190.8192 | ft
authored by Todd Miller
Not for AC circuits greater than 2,000V. This calculator does not size wire based on the greater of 125%FLA and voltage drop - just voltage drop and NEC deratings. By using this calculator you agree use it at your own risk.

## wire calculator (hidden)
| 1 | 1 | 2000 | 2000000 | 555 | 665 | 750 | 0 | 0 | 0 | 470 | 560 | 630 | 0 | 1155 | 1385 | 1560 | 0 | 0 | 0 | 960 | 1150 | 1295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2-3w L-L | 1.4142 | 1750 | 1750000 | 545 | 650 | 735 | 0 | 0 | 0 | 455 | 545 | 615 | 0 | 1070 | 1280 | 1445 | 0 | 0 | 0 | 875 | 1050 | 1185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2-3w L-N | 1 | 1500 | 1500000 | 525 | 625 | 705 | 0 | 0 | 0 | 435 | 520 | 585 | 0 | 980 | 1175 | 1325 | 0 | 0 | 0 | 795 | 950 | 1070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2-4w | 1 | 1250 | 1250000 | 495 | 590 | 665 | 0 | 0 | 0 | 405 | 485 | 545 | 0 | 890 | 1065 | 1200 | 0 | 0 | 0 | 710 | 855 | 965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3 | 1.7321 | 1000 | 1000000 | 455 | 545 | 615 | 0 | 0 | 0 | 375 | 445 | 500 | 0 | 780 | 935 | 1055 | 0 | 0 | 0 | 625 | 750 | 845 | 0 | 0.68786 | 0.69948 | 0.7111 | 0.75758 | 0.79631 | 0.83504 | 0.77626 | 0.79275 | 0.80923 | 0.87519
polar conversions array |  |  | 900 | 900000 | 435 | 520 | 585 | 0 | 0 | 0 | 355 | 425 | 480 | 0 | 730 | 870 | 980 | 0 | 0 | 0 | 580 | 700 | 790 | 0 | 0.74588 | 0.75944 | 0.77299 | 0.82722 | 0.8724 | 0.91759 | 0.87223 | 0.89267 | 0.91312 | 0.9949
|  |  | 800 | 800000 | 410 | 490 | 555 | 0 | 0 | 0 | 330 | 395 | 445 | 0 | 680 | 815 | 920 | 0 | 0 | 0 | 535 | 645 | 725 | 0 | 0.74588 | 0.75944 | 0.77299 | 0.82722 | 0.8724 | 0.91759 | 0.87223 | 0.89267 | 0.91312 | 0.9949
| 140 [ 60 ] | 60 | 750 | 750000 | 400 | 475 | 535 | 0 | 0 | 0 | 320 | 385 | 435 | 0 | 655 | 785 | 885 | 0 | 0 | 0 | 515 | 620 | 700 | 0 | 0.74588 | 0.75944 | 0.77299 | 0.82722 | 0.8724 | 0.91759 | 0.87223 | 0.89267 | 0.91312 | 0.9949
| 167 [ 75 ] | 75 | 700 | 700000 | 385 | 460 | 520 | 0 | 0 | 0 | 315 | 375 | 425 | 0 | 630 | 755 | 850 | 0 | 0 | 0 | 500 | 595 | 670 | 0 | 0.79659 | 0.81273 | 0.82887 | 0.89342 | 0.94722 | 1.001 | 0.96088 | 0.98594 | 1.011 | 1.1112
| 194 [ 90 ] | 90 | 600 | 600000 | 350 | 420 | 475 | 0 | 0 | 0 | 285 | 340 | 385 | 0 | 575 | 690 | 780 | 0 | 0 | 0 | 455 | 545 | 615 | 0 | 0.79659 | 0.81273 | 0.82887 | 0.89342 | 0.94722 | 1.001 | 0.96088 | 0.98594 | 1.011 | 1.1112
| 302 [ 150 ] | 150 | 500 | 500000 | 320 | 380 | 430 | 0 | 0 | 0 | 260 | 310 | 350 | 0 | 515 | 620 | 700 | 0 | 0 | 0 | 405 | 485 | 545 | 0 | 0.84731 | 0.86603 | 0.88475 | 0.95963 | 1.022 | 1.0844 | 1.0495 | 1.0792 | 1.1089 | 1.2276
| 392 [ 200 ] | 200 | 400 | 400000 | 280 | 335 | 380 | 0 | 0 | 0 | 225 | 270 | 305 | 0 | 455 | 545 | 615 | 0 | 0 | 0 | 355 | 425 | 480 | 0 | 0.93337 | 0.95596 | 0.97855 | 1.0689 | 1.1442 | 1.2195 | 1.1862 | 1.2224 | 1.2587 | 1.4038
| 482 [ 250 ] | 250 | 350 | 350000 | 260 | 310 | 350 | 0 | 0 | 0 | 210 | 250 | 280 | 0 | 420 | 505 | 570 | 0 | 0 | 0 | 330 | 395 | 445 | 0 | 0.99407 | 1.0192 | 1.0444 | 1.1451 | 1.229 | 1.313 | 1.2975 | 1.339 | 1.3806 | 1.5468
insulation temperature array |  |  | 300 | 300000 | 240 | 285 | 320 | 0 | 0 | 0 | 195 | 230 | 260 | 0 | 375 | 445 | 500 | 0 | 0 | 0 | 290 | 350 | 395 | 0 | 1.0801 | 1.1092 | 1.1382 | 1.2544 | 1.3512 | 1.4481 | 1.4214 | 1.4689 | 1.5164 | 1.7063
|  |  | 250 | 250000 | 215 | 255 | 290 | 0 | 0 | 0 | 170 | 205 | 230 | 0 | 340 | 405 | 455 | 0 | 0 | 0 | 265 | 315 | 355 | 0 | 1.2042 | 1.2391 | 1.2739 | 1.4134 | 1.5296 | 1.6458 | 1.6087 | 1.6654 | 1.7222 | 1.949
| insul. temperature | 75 | 4/0 | 211600 | 195 | 230 | 260 | 376.4526 | 392.3271 | 409.3355 | 150 | 180 | 205 | 294.8123 | 300 | 360 | 405 | 599.8296 | 713.219 | 941.1315 | 235 | 280 | 315 | 466.0302 | 1.3083 | 1.349 | 1.3897 | 1.5523 | 1.6879 | 1.8235 | 1.776 | 1.842 | 1.9079 | 2.1717
|  |  | 3/0 | 167800 | 165 | 200 | 225 | 326.5613 | 336.7663 | 349.2392 | 130 | 155 | 175 | 257.3938 | 260 | 310 | 350 | 511.3859 | 619.1058 | 802.7965 | 200 | 240 | 270 | 397.9966 | 1.5212 | 1.5722 | 1.6232 | 1.8272 | 1.9971 | 2.1671 | 2.1659 | 2.2517 | 2.3374 | 2.6803
| 310.15(2) @30 | 1 | 2/0 | 133100 | 145 | 175 | 195 | 284.6072 | 294.8123 | 309.5529 | 115 | 135 | 150 | 224.5109 | 225 | 265 | 300 | 442.2184 | 529.5282 | 670.131 | 175 | 210 | 235 | 345.8375 | 1.8074 | 1.8719 | 1.9365 | 2.1947 | 2.4099 | 2.6251 | 2.5658 | 2.6714 | 2.7769 | 3.199
| 310.15(2) @40 | 1.1339 | 1/0 | 105600 | 125 | 150 | 170 | 243.7871 | 259.6616 | 276.67 | 100 | 120 | 135 | 191.628 | 195 | 230 | 260 | 384.3899 | 452.4235 | 603.2313 | 150 | 180 | 205 | 298.214 | 2.0709 | 2.1484 | 2.2259 | 2.5357 | 2.7939 | 3.0521 | 3.0824 | 3.2143 | 3.3462 | 3.8738
| 310.15(3) | 1 | 1 | 83690 | 110 | 130 | 145 | 210.9042 | 223.377 | 243.7871 | 85 | 100 | 115 | 164.4145 | 165 | 195 | 220 | 332.2308 | 390.0593 | 498.9131 | 130 | 155 | 175 | 258.5277 | 2.598 | 2.7013 | 2.8046 | 3.2178 | 3.562 | 3.9063 | 3.7356 | 3.9004 | 4.0653 | 4.7248
table adjustment factors |  |  | 2 | 66360 | 95 | 115 | 130 | 181.4229 | 193.8958 | 216.5736 | 75 | 90 | 100 | 140.6028 | 140 | 170 | 190 | 289.1428 | 332.2308 | 432.0134 | 110 | 135 | 150 | 224.5109 | 3.1052 | 3.2343 | 3.3634 | 3.8798 | 4.3101 | 4.7405 | 4.622 | 4.8331 | 5.0441 | 5.8883
|  |  | 3 | 52620 | 85 | 100 | 115 | 162.1468 | 172.3518 | 188.2263 | 65 | 75 | 85 | 123.5944 | 120 | 145 | 165 | 242.6532 | 285.7411 | 370.7831 | 95 | 115 | 130 | 192.7619 | 3.759 | 3.9204 | 4.0818 | 4.7273 | 5.2653 | 5.8032 | 5.6551 | 5.919 | 6.1828 | 7.238
| open to air? | 0 | 4 | 41740 | 70 | 85 | 95 | 136.0672 | 141.7367 | 167.8162 | 55 | 65 | 75 | 106.586 | 105 | 125 | 140 | 215.4397 | 249.4566 | 315.2224 | 80 | 100 | 115 | 167.8162 | 4.5297 | 4.7298 | 4.9299 | 5.7304 | 6.3974 | 7.0645 | 7.0582 | 7.3945 | 7.7309 | 9.0763
| Al60 | 0 | 6 | 26240 | 55 | 65 | 75 | 108.8538 | 124.7283 | 132.6655 | 40 | 50 | 55 | 85.042 | 80 | 95 | 105 | 175.7535 | 187.0924 | 232.4482 | 60 | 75 | 85 | 126.9961 | 6.8517 | 7.168 | 7.4843 | 8.7496 | 9.8039 | 10.8583 | 10.8973 | 11.4315 | 11.9657 | 14.1026
| Al75 | 8 | 8 | 16510 | 40 | 50 | 55 | 86.1759 | 94.1132 | 105.4521 | 35 | 40 | 45 | 64.6319 | 60 | 70 | 80 | 120.1927 | 140.6028 | 161.0129 | 45 | 55 | 60 | 94.1132 | 10.5383 | 11.0418 | 11.5453 | 13.5594 | 15.2377 | 16.9161 | 17.1127 | 17.97 | 18.8274 | 22.2569
| Al90 | 0 | 10 | 10380 | 30 | 35 | 40 | 62.3641 | 68.0336 | 82.7742 | 25 | 30 | 35 | 49.8913 | 40 | 50 | 55 | 90.7115 | 102.0504 | 121.3266 | 35 | 40 | 45 | 71.4353 | 15.8431 | 16.6177 | 17.3923 | 20.4908 | 23.0729 | 25.655 | 25.9574 | 27.2765 | 28.5955 | 33.8716
| Al150 | 0 | 12 | 6530 | 20 | 25 | 30 | 48.7574 | 51.0252 | 61.2302 | 15 | 20 | 25 | 34.0168 | 30 | 35 | 40 | 68.0336 | 77.1048 | 88.4437 | 25 | 30 | 35 | 53.293 | 26.0354 | 27.3264 | 28.6175 | 33.7817 | 38.0851 | 42.3886 | 41.2042 | 43.3146 | 45.425 | 53.8668
| Cu60 | 0 | 14 | 4110 | 15 | 20 | 25 | 38.5524 | 40.8202 | 44.2218 | 0 | 0 | 0 | 0 | 25 | 30 | 35 | 52.1591 | 61.2302 | 66.8997 | 0 | 0 | 0 | 0 | 40.0311 | 42.0322 | 44.0333 | 52.0378 | 58.7082 | 65.3786 | 0.72946 | 0.72946 | 0.72946 | 0.72946
| Cu75 | 2 | 16 | 2580 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cu90 | 0 | 18 | 1620 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cu150 | 0 |  |  | wire sized by adjusted NEC tables 310.15(B)(16) & 310.15(B)(18) | [9 empty] | wire sized by adjusted NEC tables 310.15(B)(17) & 310.15(B)(19) | [9 empty] | by % Voltage Drop
| Cu200 | 0 |  |  | Cu60 | Cu75 | Cu90 | Cu150 | Cu200 | Cu250 | Al60 | Al75 | Al90 | Al150 | Cu60 | Cu75 | Cu90 | Cu150 | Cu200 | Cu250 | Al60 | Al75 | Al90 | Al150 | Cu60 | Cu75 | Cu90 | Cu150 | Cu200 | Cu250 | Al60 | Al75 | Al90 | Al150
| Cu250 | 0 |  |  | 250000 | 167800 | 167800 | 83690 | 83690 | 66360 | 350000 | 250000 | 211600 | 133100 | 133100 | 105600 | 83690 | 41740 | 41740 | 26240 | 167800 | 133100 | 105600 | 66360 | 83690 | 83690 | 83690 | 105600 | 105600 | 133100 | 133100 | 133100 | 133100 | 167800
control switch for insul. Temperature
| conductor A | 200
| NEC min Al | 250000
| NEC min Cu | 167800
| polar conversion | 1.7321
| power factor | 0.8
| length to load | 100
| length to source | 0
| target voltage drop | 3
| direct burry | 0
| PVC conduit | 0
| Al conduit | 0
| steel conduit | 3
| open air | 0
control switch for chapter 9 table 9
| source volts | 208
| min Al | 250000
| min Cu | 167800
| Al %VD | 1.6654
| Cu %VD | 1.5722
| Al impedance | 0.0001
| Cu impedance | 9.44e-05
| max length Al | 180.1333
| max length Cu | 190.8192
| prop. increase Al G | 1
| prop. increase Cu G | 1
| EGC Al adjusted A | 200
| EGC Cu adjusted A | 200
| EGC Al size | 4
| EGC Cu size | 6
| grounding conductor Al | 2
| grounding conductor Cu | 4
| jumper Al | 2
| jumper Cu | 4
CALCULATOR REGISTER

## Trade Size (hidden)
2000 | 2000000
1750 | 1750000
1500 | 1500000
1250 | 1250000
1000 | 1000000
900 | 900000
800 | 800000
750 | 750000
700 | 700000
600 | 600000
500 | 500000
400 | 400000
350 | 350000
300 | 300000
250 | 250000
4/0 | 211600
3/0 | 167800
2/0 | 133100
1/0 | 105600
1 | 83690
2 | 66360
3 | 52620
4 | 41740
6 | 26240
8 | 16510
10 | 10380
12 | 6530
14 | 4110
16 | 2580
18 | 1620
trade # | CM

## 310.15(b)(3)(a) (hidden)
2-3 | 1 | Note!
4-6 | 0.8 | Neutral can be disreguarded for ballanced 4 wire feeders with no harmonic distortion or noise.
7-9 | 0.7
10-20 | 0.5
21-30 | 0.45
31-40 | 0.4
41+ | 0.35
# | %

## 250.66 (hidden)
2000 | 2000000 | 3/0 | 2000 | 2000000 | 250
1100 | 1100000 | 2/0 | 1750 | 1750000 | 4/0
600 | 600000 | 1/0 | 900 | 900000 | 3/0
350 | 350000 | 2 | 500 | 500000 | 1/0
3/0 | 167800 | 4 | 250 | 250000 | 2
1/0 | 105600 | 6 | 3/0 | 167800 | 4
2 | 66360 | 8 | 1/0 | 105600 | 6
Cu trade size |  | Cu G | Al trade size |  | Al G

## 250.102(C)(1) (hidden)
2000 | 2000000 | #N/A | 2000 | 2000000 | #N/A
1100 | 1100000 | 2/0 | 1750 | 1750000 | 4/0
600 | 600000 | 1/0 | 900 | 900000 | 3/0
350 | 350000 | 2 | 500 | 500000 | 1/0
3/0 | 167800 | 4 | 250 | 250000 | 2
1/0 | 105600 | 6 | 3/0 | 167800 | 4
2 | 66360 | 8 | 1/0 | 105600 | 6
Cu trade size |  | Cu G | Al trade size |  | Al G

## 250.122 (hidden)
6000 | 800 | 1200
5000 | 700 | 1200
4000 | 500 | 750
3000 | 400 | 600
2500 | 350 | 600
2000 | 250 | 400
1600 | 4/0 | 350
1200 | 3/0 | 250
1000 | 2/0 | 4/0
800 | 1/0 | 3/0
600 | 1 | 2/0
500 | 2 | 1/0
400 | 3 | 1
300 | 4 | 2
200 | 6 | 4
100 | 8 | 6
60 | 10 | 8
40 | 10 | 8
30 | 10 | 8
20 | 12 | 10
15 | 14 | 12
Amp | Cu G | Al G

## 310.15(B)(16) (hidden)
2000 | 2000000 | 555 | 665 | 750 | 470 | 560 | 630
1750 | 1750000 | 545 | 650 | 735 | 455 | 545 | 615
1500 | 1500000 | 525 | 625 | 705 | 435 | 520 | 585
1250 | 1250000 | 495 | 590 | 665 | 405 | 485 | 545
1000 | 1000000 | 455 | 545 | 615 | 375 | 445 | 500
900 | 900000 | 435 | 520 | 585 | 355 | 425 | 480
800 | 800000 | 410 | 490 | 555 | 330 | 395 | 445
750 | 750000 | 400 | 475 | 535 | 320 | 385 | 435
700 | 700000 | 385 | 460 | 520 | 315 | 375 | 425
600 | 600000 | 350 | 420 | 475 | 285 | 340 | 385
500 | 500000 | 320 | 380 | 430 | 260 | 310 | 350
400 | 400000 | 280 | 335 | 380 | 225 | 270 | 305
350 | 350000 | 260 | 310 | 350 | 210 | 250 | 280
300 | 300000 | 240 | 285 | 320 | 195 | 230 | 260
250 | 250000 | 215 | 255 | 290 | 170 | 205 | 230
4/0 | 211600 | 195 | 230 | 260 | 150 | 180 | 205
3/0 | 167800 | 165 | 200 | 225 | 130 | 155 | 175
2/0 | 133100 | 145 | 175 | 195 | 115 | 135 | 150
1/0 | 105600 | 125 | 150 | 170 | 100 | 120 | 135
1 | 83690 | 110 | 130 | 145 | 85 | 100 | 115
2 | 66360 | 95 | 115 | 130 | 75 | 90 | 100
3 | 52620 | 85 | 100 | 115 | 65 | 75 | 85
4 | 41740 | 70 | 85 | 95 | 55 | 65 | 75
6 | 26240 | 55 | 65 | 75 | 40 | 50 | 55
8 | 16510 | 40 | 50 | 55 | 35 | 40 | 45
10 | 10380 | 30 | 35 | 40 | 25 | 30 | 35
12 | 6530 | 20 | 25 | 30 | 15 | 20 | 25
14 | 4110 | 15 | 20 | 25 | 0 | 0 | 0
16 | 2580 | 0 | 0 | 18 | 0 | 0 | 0
18 | 1620 | 0 | 0 | 14 | 0 | 0 | 0
trade size |  | Cu60 | Cu75 | Cu90 | Al60 | Al75 | Al90

## 310.15(B)(17) (hidden)
2000 | 2000000 | 1155 | 1385 | 1560 | 960 | 1150 | 1295
1750 | 1750000 | 1070 | 1280 | 1445 | 875 | 1050 | 1185
1500 | 1500000 | 980 | 1175 | 1325 | 795 | 950 | 1070
1250 | 1250000 | 890 | 1065 | 1200 | 710 | 855 | 965
1000 | 1000000 | 780 | 935 | 1055 | 625 | 750 | 845
900 | 900000 | 730 | 870 | 980 | 580 | 700 | 790
800 | 800000 | 680 | 815 | 920 | 535 | 645 | 725
750 | 750000 | 655 | 785 | 885 | 515 | 620 | 700
700 | 700000 | 630 | 755 | 850 | 500 | 595 | 670
600 | 600000 | 575 | 690 | 780 | 455 | 545 | 615
500 | 500000 | 515 | 620 | 700 | 405 | 485 | 545
400 | 400000 | 455 | 545 | 615 | 355 | 425 | 480
350 | 350000 | 420 | 505 | 570 | 330 | 395 | 445
300 | 300000 | 375 | 445 | 500 | 290 | 350 | 395
250 | 250000 | 340 | 405 | 455 | 265 | 315 | 355
4/0 | 211600 | 300 | 360 | 405 | 235 | 280 | 315
3/0 | 167800 | 260 | 310 | 350 | 200 | 240 | 270
2/0 | 133100 | 225 | 265 | 300 | 175 | 210 | 235
1/0 | 105600 | 195 | 230 | 260 | 150 | 180 | 205
1 | 83690 | 165 | 195 | 220 | 130 | 155 | 175
2 | 66360 | 140 | 170 | 190 | 110 | 135 | 150
3 | 52620 | 120 | 145 | 165 | 95 | 115 | 130
4 | 41740 | 105 | 125 | 140 | 80 | 100 | 115
6 | 26240 | 80 | 95 | 105 | 60 | 75 | 85
8 | 16510 | 60 | 70 | 80 | 45 | 55 | 60
10 | 10380 | 40 | 50 | 55 | 35 | 40 | 45
12 | 6530 | 30 | 35 | 40 | 25 | 30 | 35
14 | 4110 | 25 | 30 | 35 | 0 | 0 | 0
16 | 2580 | 0 | 0 | 24 | 0 | 0 | 0
18 | 1620 | 0 | 0 | 18 | 0 | 0 | 0
trade size |  | Cu60 | Cu75 | Cu90 | Al60 | Al75 | Al90

## 310.15(B)(18) (hidden)
2000 | 2000000 | 0 | 0 | 0 | 0
1750 | 1750000 | 0 | 0 | 0 | 0
1500 | 1500000 | 0 | 0 | 0 | 0
1250 | 1250000 | 0 | 0 | 0 | 0
1000 | 1000000 | 0 | 0 | 0 | 0
900 | 900000 | 0 | 0 | 0 | 0
800 | 800000 | 0 | 0 | 0 | 0
750 | 750000 | 0 | 0 | 0 | 0
700 | 700000 | 0 | 0 | 0 | 0
600 | 600000 | 0 | 0 | 0 | 0
500 | 500000 | 0 | 0 | 0 | 0
400 | 400000 | 0 | 0 | 0 | 0
350 | 350000 | 0 | 0 | 0 | 0
300 | 300000 | 0 | 0 | 0 | 0
250 | 250000 | 0 | 0 | 0 | 0
4/0 | 211600 | 332 | 346 | 361 | 260
3/0 | 167800 | 288 | 297 | 308 | 227
2/0 | 133100 | 251 | 260 | 273 | 198
1/0 | 105600 | 215 | 229 | 244 | 169
1 | 83690 | 186 | 197 | 215 | 145
2 | 66360 | 160 | 171 | 191 | 124
3 | 52620 | 143 | 152 | 166 | 109
4 | 41740 | 120 | 125 | 148 | 94
6 | 26240 | 96 | 110 | 117 | 75
8 | 16510 | 76 | 83 | 93 | 57
10 | 10380 | 55 | 60 | 73 | 44
12 | 6530 | 43 | 45 | 54 | 30
14 | 4110 | 34 | 36 | 39 | 0
16 | 2580 | 0 | 0 | 0 | 0
18 | 1620 | 0 | 0 | 0 | 0
trade size |  | Cu150 | Cu200 | Cu250 | Al150

## 310.15(B)(19) (hidden)
2000 | 2000000 | 0 | 0 | 0 | 0
1750 | 1750000 | 0 | 0 | 0 | 0
1500 | 1500000 | 0 | 0 | 0 | 0
1250 | 1250000 | 0 | 0 | 0 | 0
1000 | 1000000 | 0 | 0 | 0 | 0
900 | 900000 | 0 | 0 | 0 | 0
800 | 800000 | 0 | 0 | 0 | 0
750 | 750000 | 0 | 0 | 0 | 0
700 | 700000 | 0 | 0 | 0 | 0
600 | 600000 | 0 | 0 | 0 | 0
500 | 500000 | 0 | 0 | 0 | 0
400 | 400000 | 0 | 0 | 0 | 0
350 | 350000 | 0 | 0 | 0 | 0
300 | 300000 | 0 | 0 | 0 | 0
250 | 250000 | 0 | 0 | 0 | 0
4/0 | 211600 | 529 | 629 | 830 | 411
3/0 | 167800 | 451 | 546 | 708 | 351
2/0 | 133100 | 390 | 467 | 591 | 305
1/0 | 105600 | 339 | 399 | 532 | 263
1 | 83690 | 293 | 344 | 440 | 228
2 | 66360 | 255 | 293 | 381 | 198
3 | 52620 | 214 | 252 | 327 | 170
4 | 41740 | 190 | 220 | 278 | 148
6 | 26240 | 155 | 165 | 205 | 112
8 | 16510 | 106 | 124 | 142 | 83
10 | 10380 | 80 | 90 | 107 | 63
12 | 6530 | 60 | 68 | 78 | 47
14 | 4110 | 46 | 54 | 59 | 0
16 | 2580 | 0 | 0 | 0 | 0
18 | 1620 | 0 | 0 | 0 | 0
trade size |  | Cu150 | Cu200 | Cu250 | Al150

## NOT USED chapter 9 table 8 (hidden)
2000 | 2000000 | 0.00643 | 0.0106
1750 | 1750000 | 0.00735 | 0.0121
1500 | 1500000 | 0.00858 | 0.0141
1250 | 1250000 | 0.0103 | 0.0169
1000 | 1000000 | 0.0129 | 0.0212
900 | 900000 | 0.0143 | 0.0235
800 | 800000 | 0.0161 | 0.0265
750 | 750000 | 0.0171 | 0.0282
700 | 700000 | 0.0184 | 0.0303
600 | 600000 | 0.0214 | 0.0353
500 | 500000 | 0.0258 | 0.0424
400 | 400000 | 0.0321 | 0.0529
350 | 350000 | 0.0367 | 0.0605
300 | 300000 | 0.0429 | 0.0707
250 | 250000 | 0.0515 | 0.0847
4/0 | 211600 | 0.0608 | 0.1
3/0 | 167800 | 0.0766 | 0.126
2/0 | 133100 | 0.0967 | 0.159
1/0 | 105600 | 0.122 | 0.201
1 | 83690 | 0.154 | 0.253
2 | 66360 | 0.194 | 0.319
3 | 52620 | 0.245 | 0.403
4 | 41740 | 0.308 | 0.508
6 | 26240 | 0.491 | 0.808
8 | 16510 | 0.764 | 1.26
10 | 10380 | 1.21 | 2
12 | 6530 | 1.93 | 3.18
14 | 4110 | 3.07 | 5.06
16 | 2580 | 4.89 | 8.05
18 | 1620 | 7.77 | 12.8
trade size |  | Cu | Al

## chapter 9 table 9 (hidden)
2000 | 2000000
1750 | 1750000
1500 | 1500000
1250 | 1250000
1000 | 1000000 | 0.037 | 0.046 | 0.015 | 0.019 | 0.018 | 0.023 | 0.027 | 0.025
900 | 900000 | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031
800 | 800000 | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031
750 | 750000 | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031
700 | 700000 | 0.039 | 0.048 | 0.023 | 0.028 | 0.025 | 0.036 | 0.041 | 0.038
600 | 600000 | 0.039 | 0.048 | 0.023 | 0.028 | 0.025 | 0.036 | 0.041 | 0.038
500 | 500000 | 0.039 | 0.048 | 0.027 | 0.032 | 0.029 | 0.043 | 0.048 | 0.045
400 | 400000 | 0.04 | 0.049 | 0.033 | 0.038 | 0.035 | 0.054 | 0.059 | 0.055
350 | 350000 | 0.04 | 0.05 | 0.038 | 0.043 | 0.039 | 0.061 | 0.066 | 0.063
300 | 300000 | 0.041 | 0.051 | 0.044 | 0.049 | 0.045 | 0.071 | 0.076 | 0.072
250 | 250000 | 0.041 | 0.052 | 0.052 | 0.057 | 0.054 | 0.085 | 0.09 | 0.086
4/0 | 211600 | 0.041 | 0.051 | 0.062 | 0.067 | 0.063 | 0.1 | 0.11 | 0.1
3/0 | 167800 | 0.042 | 0.052 | 0.077 | 0.082 | 0.079 | 0.13 | 0.13 | 0.13 | 0.018307 | 0.0693 | 1.459
2/0 | 133100 | 0.043 | 0.054 | 0.1 | 0.1 | 0.1 | 0.16 | 0.16 | 0.16
1/0 | 105600 | 0.044 | 0.055 | 0.12 | 0.13 | 0.12 | 0.2 | 0.21 | 0.2
1 | 83690 | 0.046 | 0.057 | 0.15 | 0.16 | 0.16 | 0.25 | 0.25 | 0.25
2 | 66360 | 0.045 | 0.057 | 0.19 | 0.2 | 0.2 | 0.32 | 0.32 | 0.32
3 | 52620 | 0.047 | 0.059 | 0.25 | 0.25 | 0.25 | 0.4 | 0.4 | 0.4
4 | 41740 | 0.048 | 0.06 | 0.31 | 0.31 | 0.31 | 0.51 | 0.51 | 0.51
6 | 26240 | 0.051 | 0.064 | 0.49 | 0.49 | 0.49 | 0.81 | 0.81 | 0.81
8 | 16510 | 0.052 | 0.065 | 0.78 | 0.78 | 0.78 | 1.3 | 1.3 | 1.3
10 | 10380 | 0.05 | 0.063 | 1.2 | 1.2 | 1.2 | 2 | 2 | 2
12 | 6530 | 0.054 | 0.068 | 2 | 2 | 2 | 3.2 | 3.2 | 3.2
14 | 4110 | 0.058 | 0.073 | 3.1 | 3.1 | 3.1
16 | 2580
18 | 1620
trade size |  | PVC, Al | steel | PVC | Al | steel | PVC | Al | steel
|  | reactance |  | Cu resistance |  |  | Al resistance